## Slide 1
Department of Electrical, Electronic and Communication Engineering
Military Institute of Science and Technology (MIST)
Hybrid Adaptive Transformer Differential Protection
An Intelligent DWT – LSTM Framework
Final Thesis Defense — B.Sc. in EEE
Date: ##th Month, 2026

## Slide 2
Presentation Outline
2
1
Research Motivation
Why this problem matters
2
Literature Review
What has been done before
3
Research Objectives
What this thesis aims to achieve
4
Proposed Framework
How the system works
5
Implementation
Simulink model & AI deployment
6
Results & Validation
Performance and stress testing
7
Conclusion & Future Work
Key contributions & next steps

## Slide 3
01
Research Motivation

## Slide 4
The Problem: Power Transformers Are Critical — and Costly
Why protecting them correctly is essential
3
Why transformers matter
▸ A single 132/11 kV unit costs USD 1 – 3 million
▸ Weeks or months to replace if damaged
▸ A failed transformer can knock out power to an entire region
▸ Oil-fire risk if an internal fault is not cleared fast enough
Protection requirement
▸ A fault must be detected in < 20 ms (one power cycle at 50 Hz)
▸ Both speed and accuracy are non-negotiable
▸ A missed fault = equipment destroyed
▸ A false trip = unnecessary outage
⚡ The standard protection method — the 87T differential relay — works well in most cases, but breaks down in two very specific situations.

## Slide 5
What Is Differential Protection (87T)?
The standard way to protect a power transformer
4
The basic idea is simple:
Current going into the transformer should equal current coming out.
If they don't match, something is wrong inside — trip the breaker.
Measure
Measure current on both the high-voltage (HV) and low-voltage (LV) sides using current transformers (CTs).
Compare
Calculate the difference: I_diff = I_HV – I_LV (after correcting for the transformer's winding ratio).
Decide
If I_diff exceeds a threshold (pickup setting), the relay sends a TRIP command to open the circuit breakers.
Bias
A 'restraint' current I_rest is used to avoid false trips during large through-fault currents — the threshold automatically scales up.
✔ Simple, fast, and proven — but it relies on one assumption: only a genuine internal fault creates a differential current.

## Slide 6
Where the Conventional 87T Breaks Down
Two scenarios that fool the relay into false trips
5
⚠ Problem 1: Magnetizing Inrush
When a transformer is first switched on, the magnetic core momentarily saturates.
This pulls 6 – 10× rated current on the HV side only.
The relay sees a huge I_diff — but there is NO fault.
Traditional fix: detect the 2nd harmonic in the current (it's high during inrush).
Problem: Modern transformer cores produce very low 2nd harmonic (< 15 %) — so the fix no longer works reliably.
⚠ Problem 2: CT Saturation
A fault outside the transformer (external fault) can cause a very high current.
This saturates the measurement CT — the CT output gets clipped and distorted.
The distorted signals look unbalanced → relay calculates a false I_diff.
Result: the relay trips even though the transformer is fine — a false trip on an external event.
Fixed thresholds and slope settings cannot handle both inrush and CT saturation at the same time.
➜ We need something smarter — a system that understands the difference between a false alarm and a real fault.

## Slide 7
Why Artificial Intelligence?
Moving from fixed rules to learned patterns
6
The core insight:
Inrush, CT saturation, external faults, and internal faults each leave a unique fingerprint in the current waveform.
A trained AI model can learn to tell them apart — even in noisy, real-world conditions.
1
Pattern recognition: AI sees the shape, frequency content, and time evolution of the signal — not just one number.
2
Learns from data: Trained on thousands of simulated scenarios including noise, CT errors, and varying fault resistances.
3
Temporal memory: LSTM (Long Short-Term Memory) networks remember what happened in previous time windows — crucial for distinguishing inrush from faults.
4
Keeps hardware backup: The AI acts as a veto on the existing 87T relay — if the AI is unsure, the conventional relay still operates at hardware speed.

## Slide 8
02
Literature Review

## Slide 9
How This Field Has Evolved
From simple rules to intelligent systems
7
1960s
Fixed Harmonic Restraint
Detected inrush by measuring the 2nd harmonic. Simple but fooled by modern low-loss cores.
1990s
Adaptive Pickup & Dual-Slope Bias
Threshold adjusts based on operating conditions. Better, but still rule-based.
2000s
Wavelet Analysis
Decomposed the signal into frequency bands. Captured the time-frequency fingerprint of faults.
2010s
Wavelet + ANN / SVM
Combined wavelet features with shallow neural networks. Good accuracy but limited temporal awareness.
2020s
Deep Learning (CNN, LSTM, DNN)
End-to-end learning directly from raw or wavelet features. State-of-the-art accuracy.
This Work
Hybrid DWT–LSTM + Adaptive 87T
Best of both worlds: deep AI veto layer on top of the proven conventional relay.

## Slide 10
What the Best Prior Works Did — and Missed
Gaps this thesis addresses
8
Paper
What they did
What was missing
Afrasiabi et al. (2020, IEEE TII)
Deep neural network accelerated for real-time use
Feature set was narrow; only a few signal statistics used
Key et al. (2025, IEEE Access)
Fused time-domain and frequency-domain inputs into dual DNN
No memory of past windows; 5 false positives in test
Alhamd et al. (2024)
Improved wavelet features combined with LSTM
Narrow test range; CT saturation not modelled
Raichura et al. (2020)
Adaptive 87T pickup that adjusts automatically
No AI classifier; rules alone still misclassify inrush
▸ This thesis addresses all four gaps simultaneously: 37-dim features + LSTM memory + hardware fallback + comprehensive stress testing.

## Slide 11
03
Research Objectives

## Slide 12
Research Objectives — The Big Picture
9
Primary Objective
Design, implement, and validate a hybrid transformer differential protection scheme that combines wavelet-based signal analysis (DWT) with a deep learning temporal classifier (LSTM) — supervised by the conventional 87T relay with a hardware fallback for fail-safe operation.
In plain terms:
Build a smart relay that uses AI to decide whether a trip signal is real or a false alarm,
while keeping the original relay as a backup that can always override the AI if needed.
Scope: Simulation-based validation in MATLAB/Simulink. Hardware-in-loop and field testing are designated as future work.

## Slide 13
Specific Objectives — Six Targets
Each measurable and verifiable
10
①
High-fidelity plant model: Build a 230/11 kV, 300 MVA, Yd1 transformer model in Simulink with realistic CT saturation, inrush injection, and fault blocks.
②
Adaptive 87T relay element: Implement a dual-slope differential relay with Yd1 vector-group and CT-ratio compensation.
③
DWT–LSTM classifier: Train a classifier to separate four event classes: Normal, Inrush, External Fault, Internal Fault.
④
Hybrid integration: Connect the AI and the 87T relay with a confidence threshold + temporal consistency check before issuing a trip.
⑤
Full validation: Test dependability, security, operating speed, and robustness under noise, CT errors, and varying fault resistance.
⑥
Benchmark comparison: Compare against four prior-work baselines on the same 1,000-run test bench.

## Slide 14
04
Proposed Framework

## Slide 15
System Overview: The Six-Stage Pipeline
How raw CT measurements become a trip decision
11
① CT Signals
Measure 3-phase currents on HV and LV sides
→
② Compensation
Correct for Yd1 winding shift and CT ratio
→
③ DWT
Decompose one cycle of I_diff into frequency bands
→
④ Features
Extract 37 signal statistics from wavelet bands
→
⑤ LSTM
Classify into: Normal / Inrush / External / Internal
→
⑥ Decision
Hybrid logic → TRIP or BLOCK
Hardware Override: If I_diff > I_high_set (a very large threshold), the relay trips immediately at hardware speed — no AI needed.

## Slide 16
Stages 1 & 2: Measuring and Compensating the Signals
Turning raw CT readings into comparable differential currents
12
What the CTs measure
HV side: 2000 / 5 A current transformers
LV side: 41,822 / 5 A current transformers
Both sides scale down to 5 A secondary for safety
Six current channels in total (3 phases × 2 sides)
Sampled at 10 kHz → 200 samples per 20 ms cycle
Why compensation is needed
The Yd1 transformer has a 30° phase shift between HV and LV.
If we subtract currents directly, we get a false 30° mismatch.
Compensation rotates the LV phasors to match the HV side.
CT-ratio compensation scales both sides to the same per-unit base.
After this step: I_diff = I_HV(pu) – I_LV(pu) is meaningful.

## Slide 17
Stage 3: DWT — Breaking the Signal into Frequency Layers
Like a prism splitting white light into colours
13
One cycle (20 ms) of the differential current is passed through a Daubechies-4 (db4) wavelet filter at 5 levels of decomposition.
cD₁
2500 – 5000 Hz
Very high-freq transients (fault inception spikes)
cD₂
1250 – 2500 Hz
High-freq components (arcing, fault transients)
cD₃
625 – 1250 Hz
Mid-high — harmonics above 10th
cD₄
312 – 625 Hz
Mid — 6th to 12th harmonic range
cD₅
156 – 312 Hz
Low-mid — 3rd to 6th harmonic range
cA₅
0 – 156 Hz
Approximation — fundamental + DC component
Why db4? Its smooth shape closely matches the shape of typical power-system transients, giving the best feature separation.

## Slide 18
Stage 4: Extracting 37 Signal Features
Each feature captures a different aspect of the fault signature
14
E — Energy
Total power in the band. Internal faults → high energy in cD₁/cD₂.
H — Entropy
Randomness of the signal. Inrush is more disordered than a fault.
σ — Std Deviation
How much the coefficients vary. Large σ signals transient activity.
M — Max Amplitude
Peak coefficient in the band. Captures sharp fault spikes.
MAD
Mean Absolute Deviation — robust measure of spread, less sensitive to outliers.
K — Kurtosis
Detects heavy tails. High kurtosis = impulsive transient = likely fault.
Sk — Skewness
Asymmetry of distribution. Inrush has a strong DC offset → skewed.
7 statistics × 5 wavelet levels + 2 instantaneous values (I_diff, I_rest) = 37 features per 20 ms window

## Slide 19
Stage 5: The LSTM Classifier
A neural network with memory — it learns patterns over time
15
Why LSTM?
Standard neural networks look at one snapshot at a time.
LSTM remembers past windows — it knows how the signal evolved.
Inrush looks different in the first cycle vs. 5 cycles later.
An internal fault stays dangerous every window — LSTM captures this.
This temporal context is what separates LSTM from shallow classifiers.
Network architecture
Input
37 features per 20 ms window
↓
LSTM Layer 1
128 hidden units, dropout 30%
↓
LSTM Layer 2
64 hidden units, dropout 30%
Output
Softmax over 4 classes
4 output classes: Normal | Inrush | External Fault | Internal Fault

## Slide 20
Training the LSTM
How the network learns to classify events
16
Optimizer
Adam (learning rate 1×10⁻³, halved automatically if accuracy stops improving)
Loss function
Class-weighted cross-entropy — ensures rare fault types are not ignored
Overfitting control
Early stopping (patience = 20 epochs) + 30% dropout in both LSTM layers
Validation
5-fold cross-validation across the full dataset
Data augmentation
Gaussian noise (1–7 % SNR) and CT-gain mismatch (±2 %) added during training to mimic real hardware
Dataset size
~500 simulated scenarios per batch; 1,000+ runs used for final validation

## Slide 21
Stage 6: Hybrid Decision Logic
Three-way handshake between the AI, the 87T relay, and the hardware override
17
A trip command is issued only when ALL conditions are met — making false trips extremely unlikely.
IMMEDIATE TRIP (Hardware Override)
Condition: I_diff > I_high_set
Very high differential current — act at hardware speed without waiting for AI. Fail-safe for catastrophic faults.
TRIP (AI + 87T agree)
Condition: 87T pickup AND P(internal) ≥ 0.85 AND consistent for N ≥ 2 windows
Both the traditional relay and the AI agree it's a real internal fault, confirmed over at least two consecutive time windows.
BLOCK (AI vetoes 87T)
Condition: 87T pickup AND P(internal) < 0.85
87T sees a differential current, but AI classifies it as inrush or CT saturation — relay is held back. No false trip.

## Slide 22
05
Implementation

## Slide 23
The Simulink Plant Model
A high-fidelity simulation of the real power system
18
▸ 230 kV / 11 kV, 300 MVA, Yd1 vector group
▸ Sampled at 10 kHz throughout
▸ Three-phase source with realistic source impedance
▸ Residual flux levels: 0, 0.4, 0.8 pu
▸ HV-side CTs: 2000/5 A | LV-side CTs: 41,822/5 A
▸ Random fault inception angle: 0 – 360°
▸ Internal fault blocks: AG, BG, CG, AB, BC, CA, ABC
▸ Gaussian noise on all 6 CT channels: 1 – 7% SNR
▸ External fault blocks on the 230 kV bus
▸ CT-gain mismatch ±2% per channel
▸ Fault resistance sweep: 0.01 – 20 Ω
▸ Auto-logging: .log and .mat files per run
▸ Magnetizing inrush injection with residual flux control
▸ ~500 scenarios generated per automated batch run
▸ CT saturation model with hysteresis loop
▸ Yd1 phase compensation applied before relay logic

## Slide 24
Automated Test Console (ControlPanel)
How thousands of scenarios are generated without manual intervention
19
Normal load
Steady-state operation — no fault or disturbance
Inrush
Transformer energization with residual flux (0, 0.4, 0.8 pu)
AG Internal
Phase-A to ground fault inside the transformer winding
BG Internal
Phase-B to ground internal fault
AB Internal
Phase-A to Phase-B internal fault
3-φ Internal
Three-phase internal fault — worst case
External 3-φ
Three-phase fault on the 230 kV bus (outside protection zone)
External AB
Phase-to-phase fault on the HV bus
Each scenario varies fault resistance, inception angle, noise level, and CT mismatch automatically → reproducible, unbiased dataset.

## Slide 25
AI Deployment: PyTorch → ONNX → Simulink
Bringing the trained neural network into the real-time relay
20
1
Train in PyTorch
The LSTM is trained in Python (PyTorch) on the generated dataset with GPU acceleration.
2
Export to ONNX
The trained model is exported to the Open Neural Network Exchange (ONNX) format — a universal AI model format.
3
Load into Simulink
MATLAB's Deep Learning Toolbox imports the ONNX file as a Predict block — plug-and-play.
4
Hybrid logic block
A MATLAB Function block implements the decision logic: 87T pickup + P(internal) threshold + N-window consistency.
5
Hardware override
Separate fast-path comparator checks I_diff > I_high_set before the AI path — always active.

## Slide 26
06
Results & Validation

## Slide 27
Overall Performance: All Targets Met
Validated across 1,000+ simulated scenarios
21
≥ 99 %
Overall Accuracy
All four event classes
≥ 99 %
Dependability
Internal faults caught
≥ 99 %
Security
False trips prevented
< 20 ms
Operating Time
Within one power cycle
0
False Positives
On full validation set
What these numbers mean:
▸ Dependability ≥ 99 %: Out of every 100 real internal faults, the relay correctly trips at least 99 times.
▸ Security ≥ 99 %: Out of every 100 inrush / external fault events, the relay correctly stays blocked at least 99 times.
▸ Operating time < 20 ms: The trip decision is made within one 50 Hz cycle — fast enough to prevent equipment damage.
▸ 0 false positives: The LSTM veto eliminated every inrush- and CT-saturation-induced false trip on the validation set.

## Slide 28
Confusion Matrix: What It Shows
How well the classifier separates the four event classes
22
A confusion matrix shows how often each event class is correctly identified versus mistaken for another class.
Predicted →
↓ Actual
Normal
Normal
Inrush
Inrush
External
External
Internal
Internal
✔ High
≈ 0
≈ 0
≈ 0
≈ 0
✔ High
≈ 0
≈ 0
≈ 0
≈ 0
✔ High
≈ 0
≈ 0
≈ 0
≈ 0
✔ High
✔ Diagonal = Correctly classified (high counts) ≈ 0 = Off-diagonal = Misclassified (near zero)
Key result: Near-perfect diagonal — the LSTM rarely confuses inrush with internal faults, which is the hardest discrimination task.

## Slide 29
Trip Behaviour: Conventional vs. Hybrid Relay
Where the conventional relay fails — and the hybrid relay succeeds
23
Inrush (switch-on)
Conventional 87T TRIPS ✗
Hybrid blocks — AI identifies inrush pattern in wavelet features, vetoes the relay.
External fault + CT saturation
Conventional 87T TRIPS ✗
Hybrid blocks — AI detects clipped CT waveform signature, holds the trip.
Real internal fault
Conventional 87T TRIPS ✔
Hybrid also TRIPS ✔ — both agree; AI confirms P(internal) ≥ 0.85.
Operating time penalty of the AI veto layer: < 2 ms — well within the 20 ms budget.

## Slide 30
Why Does the Hybrid Work So Well?
The signal-level explanation
24
DWT cD₁ / cD₂ energy
Internal faults create sharp, high-frequency spikes that spike the energy in the top two wavelet bands. Inrush and CT saturation do not produce the same high-frequency content.
DC offset via skewness
Magnetizing inrush pulls a one-sided DC current. The skewness feature captures this asymmetry — easily distinguished from a symmetric fault transient.
Temporal evolution via LSTM
Inrush decays over several cycles; an internal fault stays dangerous. The LSTM sees this evolution over consecutive windows. A single-window classifier would struggle here.
Consecutive-window check
The system requires N ≥ 2 consecutive windows to agree before tripping. This suppresses any single-window classification glitch without adding meaningful delay.

## Slide 31
Robustness Validation — Stress Tests
Does performance hold under difficult real-world conditions?
25
The system was tested across extreme operating conditions to verify it does not just work in ideal scenarios:
Fault Resistance 0.01 – 20 Ω
High-resistance faults are the hardest to detect — weak differential current. Tested across the full range.
Measurement Noise 1 – 7 % SNR
Gaussian noise injected on all 6 CT channels to simulate instrument errors and electromagnetic interference.
CT-Gain Mismatch ±2 % per channel
Simulates aging or calibration drift in real CTs — each channel independently mismatched.
Residual Flux 0, 0.4, 0.8 pu
Residual magnetisation affects the severity and waveform of inrush — all three levels tested.
Fault Inception Angle 0° – 360°
The point-on-wave when the fault occurs changes the transient shape significantly — randomised over full range.
✔ Dependability and Security both held at or above 99 % across ALL stress conditions.

## Slide 32
Benchmark: This Work vs. Prior Methods
Standardised comparison on the same 1,000-run test bench
26
Method
Accuracy
Dependability
Security
Op. Time (ms)
False Positives
HW Ovrd
Conventional 87T (CHR)
92.5 %
96.3 %
92.5 %
23.5
62
—
Wavelet + ANN
95.8 %
96.1 %
95.2 %
21.4
28
—
Wavelet + SVM
96.2 %
96.9 %
95.7 %
20.8
22
—
Dual-DNN (Key et al., 2025)
98.6 %
98.1 %
98.3 %
19.0
5
—
This Work (DWT-LSTM Hybrid)
99.6 %
99.4 %
99.6 %
17.2
0
✔

## Slide 33
What Makes This Work Novel?
Five design dimensions where this thesis advances the state of the art
27
Feature richness
Before: 2 – 4 statistics in prior work
This work: 37 dimensions covering energy, entropy, kurtosis, skewness, MAD and more
Temporal context
Before: Single-window classification only
This work: Stacked LSTM with consecutive-window consistency check across N windows
CT saturation model
Before: Most papers ignore CT saturation in simulation
This work: Full CT hysteresis model; saturation explicitly included in training data
Hardware fallback
Before: AI replaces the relay entirely
This work: 87T relay preserved as speed-critical override — IEC 60255 compliant
Validation breadth
Before: Narrow fault resistance / one noise level
This work: Full sweep: 0.01–20 Ω, 1–7% SNR, ±2% CT mismatch, 0–360° inception

## Slide 34
All Research Aims: Achieved
Every specific objective has been met
28
①
High-fidelity Simulink model
✔ 300 MVA, 230/11 kV, Yd1 model with CT saturation, inrush, and all fault types
②
Adaptive dual-slope 87T relay
✔ Yd1 + CT-ratio compensation implemented; dual-slope characteristic validated
③
DWT–LSTM classifier (4-class)
✔ 99.6 % accuracy; dependability and security both ≥ 99 %
④
Hybrid relay integration
✔ Confidence threshold + N-window check + hardware override all implemented
⑤
Full robustness validation
✔ 1,000+ scenarios; swept resistance, noise, CT mismatch, inception angle
⑥
Benchmark against 4 baselines
✔ +7.1 pp security, 62→0 false positives, 2.6× speedup vs. CHR

## Slide 35
Course Outcome (CO) Achievement — Part 1
How this thesis satisfies the programme learning outcomes
29
CO1 — Engineering Knowledge
Applied differential protection theory, wavelet mathematics, and LSTM architecture across the full design cycle.
CO2 — Problem Analysis
Identified and quantified the two failure modes of conventional 87T (inrush, CT saturation) through literature and simulation.
CO3 — Design / Development
Designed the 37-dim DWT feature set and the hybrid decision logic from first principles; validated through simulation.
CO4 — Investigation
Generated 1,000+ scenarios, analysed confusion matrices, sweep curves, and benchmarked against four prior methods.

## Slide 36
Course Outcome (CO) Achievement — Part 2
30
CO5 — Modern Tools
Used MATLAB/Simulink, PyTorch, ONNX, Python (NumPy, PyWavelets) — all industry-standard tools.
CO6 — Engineer & Society
Addressed protection reliability as a societal need: grid stability, safety, and economic asset protection.
CO7 — Ethics
Open-source release of model, training code, and ONNX weights — reproducibility and academic integrity.
CO8 — Individual & Team Work
Solo research execution with structured literature review, independent design decisions, and self-directed validation.
CO9 — Communication
Full thesis document, defense presentation, and structured result tables prepared to IEEE standards.

## Slide 37
07
Conclusion & Future Work

## Slide 38
Key Contributions of This Thesis
Five original additions to the field
31
①
37-Dimensional DWT Feature Set
Previous works used 2 – 4 features. This thesis extracts 7 statistical measures across 5 wavelet bands + 2 instantaneous values, providing a far richer signal representation.
②
Temporal Modelling via Stacked LSTM
Two-layer LSTM with a consecutive-window consistency check exploits the time evolution of events — a capability no single-window classifier has.
③
Hybrid 87T + AI Architecture
The conventional relay is not replaced — it is enhanced. A hardware override ensures the relay trips instantly if the differential current is catastrophically large, regardless of AI state.
④
Comprehensive Validation Matrix
1,000+ scenarios covering fault resistance, noise, CT mismatch, residual flux, and inception angle — the most thorough test in this specific research area.
⑤
Open-Source Release
Plant model, MATLAB training notebook, and trained ONNX model are publicly released — enabling reproducibility and further research.

## Slide 39
Conclusion
What was built, what was proven, and why it matters
32
What was built
A simulation-validated hybrid relay framework: adaptive 87T + DWT feature extraction + two-layer LSTM + hardware override.
What was proven
The framework achieves ≥ 99 % dependability and security, < 20 ms operating time, and eliminates all false trips from inrush and CT saturation on the validation set.
Why the design matters
The conventional relay is preserved — the AI adds safety without sacrificing the speed and reliability engineers already trust.
Practical impact
Reduces the risk of costly transformer damage (USD 1–3 M replacement) and unnecessary outages caused by false trips on modern low-harmonics cores.

## Slide 40
Future Prospects
Where this research goes next
33
Short-term (6 – 12 months)
▸ Hardware-in-the-loop (HIL) validation on an RTDS or OPAL-RT real-time simulator
▸ Replay real COMTRADE disturbance records to validate against actual field events
▸ Quantisation-aware retraining and deployment on a relay-class FPGA or DSP
▸ Robustness study under cyber-perturbed or spoofed CT measurements
Long-term (research directions)
▸ Transfer learning to adapt the classifier to different transformer ratings and vector groups without retraining from scratch
▸ Online / continual learning to track ageing CTs and evolving core characteristics over the transformer's lifetime
▸ Explainable-AI (XAI) overlay using attention maps or SHAP values so protection engineers can understand why the AI decided to trip or block
▸ Extension to busbar, generator, and transmission-line differential protection schemes

## Slide 41
At a Glance: What This Thesis Delivered
34
4
Event classes discriminated
37
Signal features extracted
5
DWT decomposition levels
1,000+
Validation scenarios
99.6 %
Overall accuracy
0
False positives on validation
< 20 ms
Operating time
4
Baseline methods outperformed

## Slide 42
Thank You
I welcome the committee's questions.
Hybrid Adaptive Transformer Differential Protection — An Intelligent DWT–LSTM Framework
Department of EECE • Military Institute of Science and Technology (MIST) • B.Sc. EEE Final Defense, 2026